Session No.9, Paper No. 21

IS MAINTENANCE  RISK FREE?

THE PROBLEM OF OVERLOOKING HUMAN FACTORS RELATED ISSUES AT THE DESIGN STAGE IN HIGH VOLTAGE EQUIPMENT.

Clancy P. 3, Demichela M. 1, Leva M.C.2, Pirani R1.

1DISMIC Politecnico di Torino Italia

2 APRG Trinity College Dublin Ireland

3 ESBI Ireland

roberta.pirani@polito.it, micaela.demichela@polito.it

# Abstract

High voltage equipment is mostly designed according to technically prescriptive standards, requirements based on electrical engineering safety principles (e.g. CEI IEC 62271-202, High-voltage switchgear and control gear, 2006). However a more risk-based approach to standards and regulation may be advisable to enable designer and user to take an active role in establishing that their installation is inherently safe.

The use of Gas Insulated Switchgear (GIS) for instance is enabling the new substation to be housed indoors and condensed into around one quarter of the space. The manufacturers argue that design improvements in GIS make it virtually “maintenance free”, comply with all the relevant standards (IEC 62271-1, IEC 62271-203). However some of these improvements have implications for the operators that need to be taken into account. Commissioning, operational checks and inspections and the occasional maintenance interventions are activities during which the technicians need to interface with the equipment, the issues regarding the interfaces provided have been analysed to identify their relevance in the overall risk assessment of the equipment.

The scope of the present study is to verify trough a risk analysis the impacts that the issues related to deficit in ergonomic design may present for the overall availability and safety of the plant. Issues overlooked by both the technical standards and the designers.

Keywords – IEC standards, Human Factors, FMEA, Electrical Equipment

# Background

Several research projects and programs on system safety engineering and Quantitative Risk Analysis in the last 40 years offered very strong evidence of the crucial role that human and organizational factors (HOFs) play in major accidents. According to this increasing concern toward the relevance of HOFs in limiting safety performance considerable research effort has been spent worldwide in the last couple of decades. This resulted in a quite rich literature covering areas from theoretical bases, to accident investigation methods and application to major disasters, to very sophisticated modelling approaches and techniques of HOFs in Quantitative Risk Analysis and many standards trying to incorporate more physical aspects of Human factors like Ergonomics design. Nevertheless, many of the models and applications described in scientific literature demonstrate very limited impact on the technical standards applied for evaluation of safety critical equipment and procedures.

The standards used for providing requirements of High voltage equipment for instance does not take into proper account aspects related to the human limited but by no means negligible interaction with the equipment. High voltage equipment is mostly designed according to technically prescriptive standards, requirements based on electrical engineering safety principles (e.g. CEI IEC 62271-202, High-voltage switchgear and control gear, 2006). However a more risk-based approach to standards and regulation may be advisable to enable designer and user to take an active role in establishing that their installation is inherently safe.

The use of Gas Insulated Switchgear (GIS) for instance is enabling the new substation to be housed indoors and condensed into around one quarter of the space. The manufacturers argue that design improvements in GIS make it virtually “maintenance free”. However some of these improvements have implications for the operators that need to be taken into account. A GIS more compact in fact often means having less space and awkward stations for the technicians during commissioning and maintenance actions that are still required to be performed. Commissioning, operational checks and inspections and the occasional maintenance interventions are activities during which the technicians need to interface with the equipment, the issues regarding the interfaces provided have been analysed to identify their relevance in the overall risk assessment of the equipment.

The scope of the present study is to verify trough a risk analysis the impacts that the issues related to deficit in ergonomic design may present for the overall availability and safety of the plant. Issues overlooked by both the technical standards and the designers.

# The case study: need for risk informed design in GIS

The term switchgear, used in association with the electric power system, or grid, refers to the combination of electrical disconnects, fuses and/or circuit breakers used to isolate electrical equipment. Switchgear is used both to de-energize equipment to allow work to be done and to clear faults downstream. This type of equipment is important because it is directly linked to the reliability of the electricity supply.

A safe, reliable supply of electricity depends on the circuit breakers that protect our electricity grids in the event of short circuits.

A piece of switchgear may be a simple open-air isolator switch or it may be insulated by some other substance. An effective although more costly form of switchgear is gas insulated switchgear (GIS), where the conductors and contacts are insulated by pressurized sulphur hexafluoride gas (SF6).

The use of GIS rather than conventional air insulated switchgear (AIS) is enabling the new substation to be housed indoors and condensed into around one quarter of the space.

Gas Insulated Switchgear have been gradually changed over time moving towards layout that require less and less space. The manufacturers argue that design improvements in GIS include:

- More compact GIS design

- Higher performance CB’s with new arcing chambers

- Less operating energy

- Lower SF6 gas volumes

- Smaller operating mechanisms

- Combined apparatus, 3 position disconnect/earth switch

- Combined circuit breaker-disconnector solutions

But some of these improvements have implications for the operators that need to be taken into account. A GIS more compact in fact often means having less space and awkward stations for the technicians during commissioning and maintenance actions.

The figure 1 shows an overall vision of the most important components of the GIS that are involved in the commissioning and maintenance phase. Figure 1 is section of the GIS system (not to scale).

Figure 1: Cross Section View of GIS

The designers and manufacturers often refers to GIS as maintenance free, however commissioning, operational checks and inspections and the occasional maintenance interventions are activities during which the technicians need to interface with the equipment and the issues regarding the interfaces provided have been analysed to identify their relevance in the overall risk assessment of the equipment.

The scope of the study was also to verify trough a risk analysis the impacts that the issues related to a functional analysis of the equipment that overlooks the human machine interaction may present for the overall availability and safety of the plant.

The study highlights clearly that good design, taking into account all potential risks, helps to ensure safety during repair and maintenance work. It demonstrates once again the importance of taking into account human factors at the design stage of a piece of equipment; where modifications are easier to carry out and less expensive than they would be once the plant is built. The end users of the machine were actively involved throughout the whole risk assessment process and played a crucial role in ensuring an evaluation of the conditions leading to a safe commissioning and operations of GIS.

The results from the risk analysis can also be used to perform a cost-benefit analysis of the possible options to improve the ergonomic aspects to manage commissioning and maintenance of the substation and to decide which is the most cost-effective.

This study was also used to evaluate whether current standards used for the design and operation of High voltage equipment (e.g. CEI IEC 62271-202, High-voltage switchgear and control gear, 2006) are sufficiently taking into account the relevant aspects of man machine interface.

To achieve the objective, a preliminary risk assessment has been performed on an installation complying with relevant standards (IEC 62271-202 2006, IEC 62271-1 2007, IEC 62271-203 2004).

# Methods used to perform the risk analysis

The Risk Assessment was performed using an ad hoc Failure Mode and Effects Analysis (FMEA) template where the functional analysis included the human tasks as well as the technical aspects (Figure.2).

Further the Risk levels associated to each possible failure mode was obtained using the risk matrix proposed by the Military Standard MIL-STD-882. The overall method aimed at providing the assessment of a Risk Level similar to the Safety Integrity Level evaluation required by standards descending from IEC 61508 (originally developed for process plants, machineries and vehicles contain requirements and recommendations for validating safety-related electrical, electronic and programmable control systems).

The method would starts with a functional analysis of the equipment to identify all the relevant functions to be performed by the equipment or by an operator with the use of the equipment and the connected failure modes. Some of the failure modes can be determined assessing the Human Errors using the Technique for Human Error Rate Prediction (THERP) developed for the U.S Nuclear Regulatory Commission by Swain and Guttman in 1983.

Information about the order of magnitude of the likelihoods of the events was obtained using equipment reliability data (when available) and THERP for relevant human errors. While the severity was assigned using expert judgment based on the severity classifications guidelines used by the Military Standard MIL-STD-882.

The approach has proved to be flexible and it can be used at different levels of system detail.

| Id (1) | Man-machine function (2) | Link –to (3) | Failure-mode (4) | Cause (5) | Consequences (6) | Duration (7) | Times/Y (8) | Safeguard (9) | L (10) | C (11) | R (12) | Countermeasure (13) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

Figure 2: Template used for the analysis

To apply the hazard assessment matrix (table.3) to evaluate whether the risk was unacceptable or acceptable it was necessary to translate the numerical values, obtained from the quantitative analysis, in a judgment (table.1 and 2).  To make the method more efficient and to justify the choice of range in which likelihood and severity of consequences fall, we have adopted the guidelines proposed by the Military Standard MIL-STD-882.

Hazard severity

| Category | Name | Characteristic |
| --- | --- | --- |
| I (4)* | Catastrophic | Death Loss of system |
| II (3) | Critical | Severe injury or morbidity Major damage to system |
| III (2) | Marginal | Minor injury or morbidity Minor damage to system |
| IV (1) | Negligible | No injury or morbidity (first aid) No damage to system |

*index for safety standard IEC 62061

Table 1: Severity classification

Hazard likelihood

| Category | Name | Characteristic | Probability ref. [event/y] |
| --- | --- | --- | --- |
| A (5)* | Frequent | Likely to occur frequently Occurred several times in the last 5 years in the company. | > 10-1 |
| B (4) | Probable | Will occur several times in life of a component. Has occurred in the company. | 10-1 to 10-3 |
| C (3) | Occasional | Likely to occur sometimes in life of a component. Has occurred more than once in the industry. | < 10-3 |
| D (2) | Remote | Unlikely but possible to occur in life of a component. Has occurred in the industry. No damage to system | < 10-4 |
| E (1) | Improbable | Occurrence may not be experienced. Never occurred in the industry | < 10-6 |

*index for safety standard IEC 62061

Table2: Categories of probability

Hazard Assessment Matrix and Hazard Risk Index

| Frequency of occurrence | Hazard severity |  |  |  |
| --- | --- | --- | --- | --- |
|  | I Catastrophic | II Critical | III Marginal | IV Negligible |
| A - Frequent | IA | IIA | IIIA | IVA |
| B - Probable | IB | IIB | IIIB | IVB |
| C - Occasional | IC | IIC | IIIC | IVC |
| D - Remote | ID | IID | IIID | IVD |
| E - Improbable | IE | IIE | IIIE | IVE |

| RI 1 | Unacceptable |
| --- | --- |
| RI 2 | Undesirable (management decision required) |
| RI 3 | Acceptable with review by management |
| RI4 | Acceptable without review |

Table.3: Tools to define the class of risk

The quantitative analysis required to identify the likelihood and consequences related to a variety of events like failure mode of the electrical components, human error, “falls from ladders”, etc. and for this reason these values have been obtained from different sources.

Failure rate of electrical device were provided by reliability data of the manufacturer or through GESCOM data base related to reliability of the components of the Italian electricity grid provided by CESI’s report [3]. In this last case the value was not related to each single component but it refers to the whole system; from the MTTF (Mean Time To Failure) it was possible to obtain the respective failure rate using the following relation: MTTF=1λ.

Likelihood of events like “falls from ladders” derives from expert judgment and from records of worker’s injury reported by the company involved in the analysis [5].

The failure rate values associated to human error were obtained through the application of THERP model.

Each mean HEP was modified by the effects of unfavorable ergonomics conditions stress and experience level could also be taken into account in case of emergency conditions. (THERP table 20-16 in Swain and Guttman 1983).

The likelihood obtained was also discounted to take into account the actual timeframe over which certain tasks are carried out in the life period of the equipment (e.g. commissioning is 1/ 30 years, where 30 years is the expected life duration of the equipment, and Maintenance interventions 1/ 5 years)

# Overview of the results from the analysis

The study shows that the most significant issues are:

- often limited and restrictive working areas;

- the limited possibilities for applying forces;

- the need for the technicians to work in fixed and awkward posture for sustained periods of time,

- difficulty or complete inability of reading the metrological data,

- slowdown in emergency procedure.

Most of these issues are ergonomic aspects and they have an important relapse on reliability of the whole system and on the wellbeing of the operators.

The bays of the substation are very close to each other and there is not enough space for the operator to access some of the equipment located in between the bays.

Fig. 3: Awkward position of the indicator (above 2mt. high and difficult to read in between bays)

It seems that some basic principles of accessibility were not properly taken into account in the design of the equipment. The lack of basic ergonomics principle in design is reflected in the difficulties encountered by the operators to manually open or close the circuit breakers in case of failure of automatic activation. The risk is that the worker fails to resolve situation in time because he/she must reach the high location and turn the mechanism shaft while standing in an awkward position. Furthermore if the operations has to be performed for bays internally located the operator has to climb over the pipelines containing the live cables and the insulating Gas. No platforms were in fact provided to access those areas.

Fig. 4: Cables to be reached during commissioning and testing. The picture shows that they are positioned in a confined area accessing which the operator needs to maintain a crawling awkward position.

Fig. 5: Operator trying to reach while standing on a ladder the manual gear to open the switch in case of failure of the automatic system for the side bay.

The results of the first step of the analysis are confirmed and supported by a survey of users of GIS carried out by the Committee of the Institute of Electrical and Electronics Engineers (IEEE 2010) [10].

The survey highlights once again issues like:

- constricted space for maintenance;

- awkward accessibility of view port;

- difficulty to read SF6 gas pressure gauges.

Comparing the free space required for different dynamic body postures which may be used during maintenance with moderate force demands, indicated by ergonomic standard ISO 14738:2008 with some positions in working area of GIS the dimensions seem to be underestimated. This can lead to serious musculoskeletal problems for the operator and could lead the worker to commit a mistake during the relevant commissioning, testing or recovery tasks he or she has to perform.

Fig.6: Image taken form the ergonomic standard ISO 14738:2008 showing dimensions for kneeling and crawling positions. Unfortunately the height is not indicated.

The results provided by the quantitative analysis suggest two types of consequences. The first is related to the underestimation of the risk associated with the loss of primary functions of the plant normally achieved with a traditional FMEA, the failures connected to loss of efficiency, possible disruption to customers seems to be much higher and diverse than the one normally considered in common FMEA performed on that type of equipment (see Buakaew 2010). The other consequence specifically highlights the impact of ergonomic constraints on the operator,

Once applied the hazard assessment matrix the hazard risk index for each failure mode falls into two different classes: Risk index 1 and Risk index 2

One is unacceptable (Risk index 1), this index was usually obtained for cases where the ergonomics constraints made it nearly impossible for the operator to effectively carry out his/her task. The other risk index commonly obtained (Risk Index 2) refers to undesirable situations where the operation is possible but awkward to perform such that the operator may be more easily induced to make mistakes. In those cases the consequences are severe both for the operator safety and for the plant efficiency.

In case of undesirable risk, management decisions on possible corrective actions are required.

Table 4 contains an extract of the results obtained for the risk Assessment of the GIS with some examples of the failure modes leading to a risk index 1 or 2.

| id | Man-Machine function | Failure mode | Causes | Consequences | L | C | R |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 6 | Visual inspections |  |  |  |  |  |  |
| 6.1 | Take counter reading if cycles above 10.000 perform minor maintenance | Operating cycle counter does not work | Operating linkage is loose or defective operating cycle counter is defective | Incorrect maintenance | B | III | 2 |
|  |  | Operator can not see the counter | Awkward reachability | Incorrect maintenance |  |  |  |
| 6.2 | Circuit breaker and motor wound mechanism |  |  |  |  |  |  |
| 6.2.1 | Inspect cabinet(free of damages), check heater functions, verify ventilation opening allow free air movement, examine view windows must be clear of dust and moisture | Operator fail to make the checks | The window to be checked and the ventilation opening are not easily reacheable | Presence of moisture in the breaker can go undetected resulting in Incorrect operation of protection. | B | II | 1 |

Tab.4: Table reporting an extract of the FMEA performed on the GIS

# Conclusions

The analysis results confirm the first hypothesis; the accessibility of the GIS presents different crucial aspect that the basic standard IEC 62271-1, IEC 62271-203 and the manufacturer don’t take into account.

The technical regulation IEC related to GIS is not completely exhaustive for the aspects of detail affecting the management of GIS. It does not provide any clear approach to do the risk analysis.

Taking into account human factors during the risk analysis the level of risk change significantly, in some cases also of an order of magnitude going from acceptable risk to undesirable or in the worst case to unacceptable.

The results show that more exhaustive evaluation is necessary and that the interface between the operator and the equipment cannot be negligible.

To achieve useful results could be necessary to apply approaches similar to the one proposed for the Safety Integrity Level related to machinery tailored for high voltage equipment.

In the specific case of GIS some technical specifications exist (Terna 2010) [16] and gives some interesting guidelines that could be taken into account to improve the accessibility of the bays.

The results were discussed in a review meeting with operational personnel and the safety supervisor of the company interested in this issue. They approved and confirmed the problems highlighted by the analysis and will use them to try and identify feasible solution with the management.

# References

- Buakaew S., Reliability Centered Maintenance For Gas Insulated Switchgear Maintenance, Conference Proceedings CEPSI 2010 Taipei on October 24-28, 2010

- CEI IEC 62271-202, High-voltage switchgear and control gear, 2006.

- CESI Report, Development of processing tools with a limited but significant data, 2005.

- EN IEC 61508, Functional Safety of Electrical/Electronic/Programmable Electronic Safety-related Systems, 2010.

- ESB, Injury statistics of ESB staff, 2009

- German D., Blackman H., Human Reliability & Safety Analysis Data Handbook, John Wiley & Sons, 1994.

- IEC 62271-1, High-voltage switchgear and controlgear - Common specifications, 2007.

- IEC 62271-202, High-voltage switchgear and control gear, 2006.

- IEC 62271-203, Gas-insulated metal-enclosed switchgear for rated voltages above 52 kV, 2004.

- IEEE, Gas insulated substation experience feedback, IEE/PES Substation Committee, 2010.

- Kirwan B., Ainsworth L., A guide to task analysis, Taylor & Francis, 1992.

- MIL-ST_1472, Human Engineering, Department of defence design criteria standard.

- MIL-STD-882, System Safety Program Requirements, 1993.

- NUREG 0700, Human system interface design review guidelines, 2002.

- Swain A. D., Guttmann H.E., NUREGCR 1278F, Handbook of human reliability analysis with emphasis on nuclear power plant application (final report), 1983.

- Terna, Technical specifications- Prefabricated equipment with isolated metal closure with gas SF6 for ratings equal or higher than 140 kV, 2010.