Session No.6, Paper No.15

Electrical Substation Maintenance Strategies and Methods

<Didier Margraitte>1 , <Eric Ravoir> 2

1<ALSTOM Grid>, <France>

2<ALSTOM Grid>, <France>

didier.margraitte@alstom.com

eric.ravoir@alstom.com

# Abstract

The HV electrical substations are split in two main families: the Air Insulated Substations and the Gas Insulated Substations. The first ones were energized a long time ago, in 20s for the AIS and in 70s for the GIS.

A HV substation is a strategic outfit within a global Grid. It is a key interface between the Power Plants, the Distribution nodes and the Consumers. If the HV substation is not correctly maintained, there are direct negative and huge impacts on the energy supply quality, as well as negative financial and brand image impacts for Companies like Utilities, Producers, Industrials.

A HV substation includes several types of equipments:

- HV equipments like: busbars, power transformers, disconnectors, insulators, circuit breakers, cables, OHL, surge arrestors, measurement reducers, …

- LV equipments like Control, protections or Telecom devices.

Also, many different materials and technologies are mixed in a same substation, i.e. : oil, copper, aluminium, SF6 gas, electronic components, …

Within a same place, the required features, the expected performances and the operating modes of the electrical equipments are very different. It is why the needs and the means of maintenance are specific for each of them. It is true all the more as each category of equipment has its own lifecycle. This involves several levels of consideration due to the complete heterogeneous panel of equipments to maintain. Some audit methods help to anticipate the best approach for each component of the substation.

The new technologies, based on Intelligent Electronic Devices (IED) combined with SCADA interfaces and Smart Grid solutions, offer a large panel of merged solutions for the asset management. Based on periodic surveys to evaluate the criticality levels of each equipment, these technologies support the maintenance staffs on continuous improvement action plans from the curative maintenance up to the condition monitoring, by considering as well intermediate levels like predictive maintenance, repair and retrofit.

High level Expert tools help the maintenance teams to anticipate and prevent all minor and major damages, in accordance with the International Environmental Rules. In the same time, the recent technologies of communication (like IEC 61850 protocol) offer the possibility to facilitate the monitoring with remote and local actions.

For technical as well as financial reasons, the question of life extension of the electrical infrastructures is key for most of the Companies all over the world. This is in the top list priorities of Alstom Grid to focus on development of new technologies and solutions, in order to support and facilitate the asset management, and improve the cost efficiency of the maintenance action plans to be addressed to these Companies.

The communication will address the description of the problems, the audit concepts, the new monitoring solution, and the maintenance strategy to adapt to optimize the life cycle and related costs.

Keywords – HV substations, Maintenance, Asset Management, Monitoring, IED’s, Lifecycle

# I. Introduction

# II. Maintenance strategy

II.I. 	Electrical substation: a critical infrastructure

II.II. 	Maintenance strategy criteria selection

II.III. 	Methodology to build the maintenance model

II.IV. 	Standard substation maintenance models

# III. Audit concepts

III.I. 	Approach

III.II.	Decision tool

III.III.	Benefits for the user

# IV. Monitoring solutions

IV.I. 	Smart Grid Concept

IV.II.	Examples of application (GIS)

IV.III   Operation & Maintenance Expert tools

IV.IV.	Objectives and benefits

# Summary & Conclusion

# I. Introduction

The HV electrical substations are split in two main families: the Air Insulated Substations and the Gas Insulated Substations. The first ones were energized a long time ago, in 20s for the AIS and in 70s for the GIS.

A HV substation is a strategic outfit within a global Grid. It is a key interface between the Power Plants, the Distribution nodes and the Consumers. If the HV substation is not correctly maintained, there are direct negative and huge impacts on the energy supply quality, as well as negative financial and brand image impacts for Companies like Utilities, Producers, and Industrials.

For example, when GIS technology was introduced in the early 70’s, the equipment was expected to operate satisfactorily for a period of 25 years. Since the 90’s, the positive return from the field has encouraged GIS Manufacturers to extend the life expectancy of their equipment to 40 years.

Today, it has been widely observed and confirmed by international surveys that the equipment is still in very good condition of operation wherever a suitable maintenance policy is implemented. Thus, it is quite realistic to push forward beyond the 40-year life expectancy of a GIS, which has had:

- An ad hoc long-term service agreement set up between the GIS supplier and the end-user.

- A relevant life extension strategy, which reflects the practical management of the obsolescence of the components.

Economic constraints can also lead to extending the life-duration of equipment and the obsolescence issue is clearly part of asset management.

Depending on the critical importance of the equipment and the consequences due to unavailability, life extension can broadly encompass two strategies: ‘reactive’ or ‘preventive’.

Reactive strategies consist of working on alternative solutions when obsolescence is detected. This requires time, or action, in order to define, qualify and implement the future alternative solutions.

Preventive strategies consist of anticipating the obsolescence in order to reduce potential impacts or probabilities of occurrence.

Whether reactive or preventive, a large range of solutions can be considered:

- Strategic spare parts stock

- “Industrial alternatives” spare parts policy i.e. replacement of minor components by those from the latest generation

- “Industrial alternatives modernization concept” i.e. replacement of the major components of an existing GIS by those from the latest generation

- _ …/…

# II. Maintenance strategy

II.I. 	Electrical substation: a critical infrastructure

Electrical substations are the most critical part of an electrical transmission or distribution grid. A failure of a single piece of substation equipment can cause a total grid collapse which may take days or even longer to rectify. For this reason, substation care is one of the most important parts of any electrical maintenance department.

Insurance companies estimate the transformer failure generates:

- 50 % of revenue loss in Power Generation sector

- 10 % of revenue in chemical industries

- 7 % in paper mills industry

- 6 % in other activities

Fig. 1 – Transformer catastrophic failure

Considering these high impact of a bad maintenance policy on the asset lifecycle and on the indirect consequences, a proper maintenance strategy has to be implemented. Various models are applicable depending on the nature of the asset, its criticality, and its age.

II.II. 	Maintenance strategy criteria selection

Many parameters influence the performance and the value of the equipment in a substation. The major one is directly related to the life cycle, older the asset are, high the maintenance cost is, and lower the direct value remains. At any time the maintenance approach can be challenge by other alternatives from doing nothing and manage the risk to replace the assets by new one.

To determine the strategy, the first step consists to understand the substation current performance. Data needs to be defined and collected, to measure this current status.

Then, to assess the right tools and means, the expected future performance has to be defined. The gap between initial and expected status will drive the maintenance strategy through detailed actions, inspection plan or routines.

Fig. 2 – Assets performance and value as driver

II.III. 	Methodology to build the maintenance model

A good maintenance model has to rely on tangible data giving the image of the asset status. The requested data have to be defined according to their availability in the substation. The range of data is very large, and can come from periodic visual inspection in a time-based maintenance model, to a very sophisticated sets provided by sensors in a conditioned based model.

Once these data available and collected, a suitable methodology has to be implemented to determine the best action to perform according to the measured value (tuning, repairs, partial retrofit, etc). The actions take also into consideration the admissible risk level to optimize the maintenance cost and link it with the asset value and/or the failure cost.

Then, a return on experience helps to understand the efficiency of the selected model> Adaptations will be implemented, requiring sometime new data, and new methods,

Fig. 3 – Model loop to assess maintenance methods

II.IV. 	Standard substation maintenance models

Substation most standard maintenance approach is based on a process of periodic, planned inspection of and, if necessary, repairs, and replacement of all switchgear, transformers, buildings, and ancillary equipment in substation installations. In simple terms, substation maintenance is a set of regular preventative checks and actions carried out to ensure substations are kept in good operation status. This process typically consists of a series of visual and physical inspections (audits) and actions carried out according to a set schedule. All inspection and actions during substation maintenance should be accurately documented and stored for further reference.

Routine or minor substation maintenance is usually carried out on a yearly or bi-yearly basis. It typically consists of visual checks and superficial cleaning only. Checks would include visual confirmation of the general condition of switchgear, earthing mechanisms, transformers, insulating liquid levels, and lightning arrestors. A general system performance check can also be carried out using any installed software or by reviewing incoming and outgoing meter readings. These checks are generally implemented in accordance with a set checklist and all findings are noted and filed.

More critical is the asset, more a continuous checking is valuable. This is particularly true for Gas Insulated Substations and for Power Transformers, where Condition Monitoring devices will offer a much optimized maintenance in term of cost, outage and lifecycle extensions. Detailed examples are addressed in this paper.

Fig. 4 – Some standard models

# III. Audit concepts

III.I. 	Approach

To assess the initial or current performance of a substation, the audit is the most used way to collect data. The method is based on Inspection check lists and scales to determine status.

Our approach is to determine the performance on all major parts of the substation:

- Buildings

- Transformers

- HV systems

- MV systems

- LV systems

- Cables and connections

- Power Supply

- Compensation

- Environment

- Earthing

II.II.	Decision tool

In our audit tool, we measure or control around 150 items visually, or using convenient tools). Any result provide a mark, this mark can be considered as critical or not.

Fig. 5 – Example of a Transformer assessment

For any controlled item, a decision to implement corrective or preventive actions can be decided. The tool allows to track these actions and to analyze their efficiency when the return on experience is performed.

A multi-year tracking report is provided, showing is a simple manner the impact of the maintenance actions and methods used.

Fig. 6 – Tri-annual assessment example

III.III.	Benefits for the user

A visual spider-chart shows the evolution, year per year, of the status of the different asset in the substation.

This help to decide on future maintenance actions, on maintenance policy evolution, and on planned investments.

# IV. Monitoring solutions

IV.I. 	Smart Grid Concept

Transmission systems and their equipment have been designed for reliability.

Energy managers require cost-effective applications and solutions to avoid any unscheduled gas-insulated substation downtime, major failure and subsequent penalties.

Smart grid is a type of electrical grid which attempts to predict and intelligently respond to the behaviour and actions of all electric power users connected to it - suppliers, consumers and those that do both – in order to efficiently deliver reliable, economic, and sustainable electricity services.

In Europe, the smart grid is conceived of as employing innovative products and services together with intelligent monitoring, control, communication, and self-healing technologies in order to:

- Better facilitate the connection and operation of generators of all sizes and technologies;

- Allow consumers to play a part in optimizing the operation of the system;

- Provide consumers with greater information and options for choice of supply;

- Significantly reduce the environmental impact of the whole electricity supply system;

- Maintain or even improve the existing high levels of system reliability, quality and security of supply;

- Maintain and improve the existing services efficiently;

IV.II.	Example of application:

The most effective solution to avoiding potential GIS failure is through  Condition-based asset management with advanced detection. This is

why ALSTOM GRID has developed a wide range of AIS and GIS monitoring system. The system is easy to adapt to switchgear types, is cost-effective and reliable.

The product embedded in the monitoring system are digital, open and modular.

The figure below represents a conceptual view of the preferred architecture. This conceptual architecture is described in additional detail in the following lines.

The Online Condition Monitoring System (“The System”) consists of the following

major components:

a. Condition Monitoring Devices (“CMD”)

- Measurement Sensor (“Sensor”)

- Intelligent Electronic Device (“IED”)

b. Communication Gateways

- Substation Gateway (“SG”)

- Enterprise Gateway (“EG”)

c. Central Monitoring System (“CMS”)

- Condition Monitoring Server (“CM Server”)

- Condition Monitoring Client (“CM Client”)

- Condition Monitoring Application Software (“CM Application”)

d. System Interface

- Interface with Remote Terminal Unit (RTU) or Intelligent Protection, Automation, Control and Supervision System (IPACS) for Alarm generation (“Alarm Interface”)

- Interface with OSIsoft PI Historian (“PI Interface”)

“Field Devices” refer to the components locating at substations level, e.g. Switchgear Room and Control & Protection Room, including Condition  Monitoring Devices, Substation Gateways, Local HMI, and other accessories.

“Backend System” refers to the components locating at enterprise level, e.g. Office or Data Centre, including Enterprise Gateway, Central Monitoring System, and PI Interface.

IV.III.	Operation & Maintenance Expert tools

Illustration with the SF6 Monitoring:

Apart from the possibility of performing alarm functions on thresholds and having real-time measurements of the density of the gas providing equipment insulation, digital monitoring systems offer other opportunities via their recording and calculation potential:

- monitoring of dynamic phenomena such as "catastrophic" type leaks that may occur following an accident, and putting cut-off safety mechanisms into place;

- monitoring of medium and long term trends.

With traditional monitoring solutions, you can make periodic measurements, but it is not possible to make reliable estimations of the long-term trend. And these measurements must be made, particularly outdoors, under strictly identical operating conditions. On the other hand, digital solutions offer the power of calculation tools applied to a leak detection algorithm which:

- ignores aberrant records;

- detects gas treatments and particular points;

- performs statistical analyses on the data.

The following example (Figure 4) shows density records performed on the three phases of a long GIL, which is divided into interior and exterior sections.

Due to the dispersal of the records, an expertise tool can effectively meet the requirement to accurately determine long-term trends. Modern monitoring solutions authorize much more reliable interpretations than traditional solutions as they are based on digital processing: processing validated in the development phase by simulation applications generating random scenarios or using feedback originating from the different sites in operation.

As a large proportion of the routines used in the leak detection algorithm are based on statistical treatments, it is easy to establish a periodical SF6 budget in the form of online indicators. Figure 5 shows an example of two types of indicator inferred from analyses performed over a period of 5 years on a typical GIS:

- the change in SF6 emissions into the atmosphere over several successive years;

- the distribution of leakage rates per compartment over several successive years;

Finally, these indicators enable operators to rationalize their SF6 policy by anticipating the maintenance plans and optimizing the SF6 stocks reserved for them. Early monitoring from the assembly phase, also with the aim of increasing the availability of old GISs/GILs, offers the opportunity to improve installation qualities.

IV.IV.	Objectives and benefits

The main objectives reached with a smart-grid solution are listed below :

- Reach operational efficiency

End-to-end solutions: Consulting, design and a comprehensive range of products, solutions and services.

- Increases network availability and reliability

- Model-based analysis

Allows preventive failure detection, and helps the operator to take preventive actions and mitigating potential blackouts.

- Optimal investment decisions :

By avoiding unnecessarily oversized investments, and reducing maintenance costs

- Excellent asset management

Environmentally friendly and monitoring operations under all conditions

# Summary & Conclusion

Electrical substations are complex and critical infrastructures. To maintain such assets, many alternatives are possible. The implementation of the best maintenance approach needs to rely on:

- the full life cycle cost

- the age of the equipment

- the current and expected performance

More and more, a continuous assessment of the key equipment status (Transformers, Circuits Breakers, SF6 insulated devices) will help to optimize the maintenance cost, giving data to perform the convenient action at the right moment.