Session No.6, Paper No.16

Energy Performances Contracting

Cristina ZAHALCA

ZÊTA Consulting, France

contact@zeta-consulting.fr

# Abstract

Born to the Grenelle Environment Forum, the Energy Performance Contracting (EPC) is a means of implementing energy efficiency and reducing operating costs with no up-front cost. The EPC provides a full range of services, which can include design, construction and maintenance.

The aim of this paper is to present some Reliability and Maintainability performance questions of the Energy Service Company (ESCO) during the feasibility phase of a restricted industrial project. It is well known that all additional maintenance activities and the lack of performances guaranties will be associated to important penalties. The already-realized ESCO’s audit over the installation covered by the EPC shows that the heating, ventilation and air-conditioning (HVAC) could be presented hereafter as a significant example of the ESCO’s problems.

This paper gives details about the activities of the ESCO’s energy auditor and RAM engineer during the feasibility phase of the EPC’s project: the EPC’s installation audit, the Reliability – Maintainability & Criticality audit, the selection of the appropriate maintenance policy and tasks, …The Weibull parameters estimation done by the ESCO’s RAM engineer are compared to similar values of similar known equipment. The actual Logistic breakdown and Maintenance Plan will be also reviewed by ESCO before the maintenance cost estimations and RAM performance engagements.  The maintenance and operation errors on the actuals equipment are significant.

A wished new stress model adapted to the HVAC equipment under the new mission more energy efficient is not yet developed, this modeling shall be done the next year adapted to the “old” HVAC’s failure database and all Computerized Managed Maintenance System (CMMS) information recorded over the last five years.

Keywords – Energy performances; Energy Performances Contracting; Energy Services Company (ESCo), greenhouse gases; Heating, Ventilation and Air-Conditioning (HVAC), International Performance Measurement and Verification Protocol (IPMVP); Preventive maintenance; Weibull parameters

# Introduction

The Grenelle Environment Forum confirme it: the energy efficiency, and quite particularly in the sector of the building, constitutes the main priority of the fight against climate change French policy. This paper presents some ESCO activities during the feasibility phase of an EPC in order to cover, in a preventive way, all the non-compliances of the performance engagements caused by low reliability or maintainability performances of the EPC’s equipment and maintenance personnel.

# Energy Efficiency Plan 2011

On 8 March 2011, the European Commission has adopted the Commu-nication "Energy Efficiency Plan 2011” [1]. The energy efficiency is one of the most cost effective ways to enhance security of energy supply, and to reduce emissions of greenhouse gases and other pollutants. The Union has set itself a target for 2020 of saving 20% of its primary energy consumption compared to projections (“20-20-20” objectives).

- The greatest energy saving potential lies in buildings. The plan focuses on instruments to trigger the renovation process in public and private buildings and to improve the energy performance of the components and appliances used in them.

- Transport has the second largest potential.

- Energy efficiency in industry

The Energy Performance Contracting (EPC) is an important tool in the refurbishment of buildings. Under this performance-based form of purchasing, monetary savings from lower utility bills and maintenance costs that result from energy efficiency measures are used to cover part or all of the measures' investment costs.

# Energy Performance Contracting (EPC)

## A. Energy Performance Contracting (EPC) definition

The Energy Performance Contracting (EPC) is characterized by the implementation of actions leading to the energy effectiveness amelioration through a verifiable and a measurable way, matched by a guarantee of results, during all the contract period, brought by the EPC’s operator. 
The EPC links the EPC’s operator to its customer which could be the owner or administrator of the buildings (private or public) in residential, 
service or industrials sectors.

## B. Energy performance of buildings and building units

The buildings sector represents 40% of the European Union’s (EU) total energy consumption. The Directive 2010/31/EU of the European Parliament and of the Council of 19 May 2010 [2] on the energy performance of buildings contributes to achieving this aim by proposing guiding principles for Member States regarding the energy performance of buildings.

The energy performance of a building is the calculated or measured amount of energy needed to meet the energy demand associated with a typical use of the building, which includes energy used for heating, cooling, ventilation, hot water and lighting.

## C. Methodology for calculating the energy performance of buildings

The European Union’s (EU) member shall adopt a methodology for calculating the energy performance of buildings which takes into account certain elements, specifically: the thermal characteristics of a building (thermal capacity, insulation, etc.); heating insulation and hot water supply; the air-conditioning installation; the built-in lighting installation; indoor climatic conditions. The positive influence of other aspects such as local solar exposure, natural lighting, and electricity produced by cogeneration and district or block heating or cooling systems are also taken into account. The European Union’s (EU) member are also responsible for putting in place a system of regular inspections of heating and air-conditioning systems (HVAC) in buildings.

# Energy Service Company (ESCO)

An energy service company (acronym: ESCO or ESCo) is a commercial business providing a broad range of comprehensive energy solutions including designs and implementation of energy savings projects, energy conservation, energy infrastructure outsourcing, power generation and energy supply, and risk management. The ESCO performs an in-depth analysis of the property, designs an energy efficient solution, installs the required elements, and maintains the system to ensure energy savings during the payback period.

## A. Energy saving tracking method

After installing the energy conservation measures (ECMs), the savings created from the project must be determined. This process, termed Measurement and Verification (M&V), is frequently performed by the ESCO. The International Performance Measurement and Verification Protocol (IPMVP) is the standard M&V guideline for determining actual savings created by an energy management program. IPMVP provides 4 methods for using measurement to reliably determine actual savings.

## B. Developing a project

The energy savings project often begins with the development of ideas that would generate energy savings, and in turn, cost savings. This task is under the responsibility of the ESCO. During the initial period of research and investigation, an energy auditor from the ESCO surveys the site and reviews the project's systems to determine areas where cost savings are feasible, usually free of charge to the client. Then, the ESCO’s engineers are responsible for creating cost-effective measures to obtain the highest potential of energy savings. These measures can range from highly efficient lighting and heating/air conditioning upgrades, to more productive motors with variable speed drives and centralized energy management systems. There is a wide array of measures that can produce large energy savings.

Once the project has been developed and a performance contract signed, the construction or implementation phase begins. Following the completion of this phase, the monitoring and maintenance or measurement and verification (M & V) phase begins.

## C. ESCO’s engagements

In the client point of view, the better ESCO shall Identify and evaluate energy-saving opportunities; develop engineering designs and specifications; manage the project from design to installation to monitoring; arrange for financing; train the staff and provide ongoing maintenance services; guarantee that savings will cover all project costs.

# ESCO’s works during the feasibility study

This paper’s aim is to develop some ESCO’s problems that concern the ongoing maintenance services according the maintenance cost estimation made respecting the EPC’s performances terms. The EPC’s performance objectives shall conduct to a maintenance services cost reduction.

During the initial period of research and investigation, the ESCO’s energy auditor will be accompanied by a RAM engineer who shall investigate: the maintenance candidates, the associated preventive and correctives tasks, the causes of the incidents requiring equipment replacing, the client’s reports concerning the premature aging, …

The table (figure 1) below presents the planning and the main tasks and documents of the ESCO’s energy auditor and the RAM engineer missions.

| Step | Detail | Analyze | Optimization way |
| --- | --- | --- | --- |
| 1 | Analyze of the EPC’s performances |  |  |
| 1.1 | What is the required availability? | y |  |
| 1.2 | What is the required maintainability? | y |  |
| 1.3 | What is the required reliability? | y |  |
| 1.4 | What is the expected life? | y |  |
| 1.5 | What is the reduction maintenance cost objectives? |  | Y |
| 2 | Carry out the EPC’s installation and its equipment audit |  |  |
| 3 | Carry out the RAM & criticality audit |  |  |
| 3.1 | Logistic breakdown | y |  |
| 3.2 | Computerized Maintenance Management System (CMMS) | y |  |
| 3.3 | Actual R & M estimations | y |  |
| 3.4 | Incidents database, FMECA, Root cause analysis | y |  |
| 3.5 | Maintenance history, Pareto analysis | y |  |
| 3.6 | Reports of premature aging | y |  |
| 3.7 | Comparison with EPC’s R&M database |  | y |
| 3.8 | Review of the Reliability and lifetime estimation |  | y |
| 4 | Select appropriate maintenance policy and task |  |  |
| 4.1 | Review of the logistic breakdown |  | y |
| 4.2 | Review the condition monitoring task |  | y |
| 4.3 | Review the inspections task |  | y |
| 4.4 | Review the preventive maintenance task |  | y |
| 4.5 | Review the corrective maintenance task |  | y |
| 4.6 | Introduction of the maintenance tasks for the new equipment | y |  |
| 5 | Update the Maintenance Plan |  |  |
| 5.1 | Estimate/update the maintenance job/task |  | y |
| 5.2 | Estimate/update the human resources |  | y |
| 5.3 | Schedule/update the preventive & corrective maintenance |  | y |
| 6 | Review the EPC’s performances |  | y |
| 6.1 | Review the EPC’s installation and RAM’s performances |  | y |
| 6.2 | Percentage of Preventive versus Corrective maintenance |  | y |
| 6.3 | Spare used |  | y |
| 6.4 | New maintenance budget estimation |  | y |
| 6.5 | Percentage actual/new maintenance budget |  | y |

Figure <1: Example detail of the EPC’s energy auditor and RAM engineers program >

# HVAC systems

## A. Carry-out EPC’s installation and its equipment audit (Step 2)

The paragraph below presents more details of the Step 2 audit results concerning the Heating Ventilation and Air Conditioning (HVAC).

It is considered that the heating, ventilating, and air-conditioning (HVAC) is the key to maintaining a comfortable, healthy and productive work environment. The HVAC constitutes up to 40 % of energy used. This fact sheet is geared towards energy efficiency in existing equipment and covers common opportunities for facilities to conserve energy and cut costs.

When the opportunity exists, energy conservation should be a factor in the equipment selection and system design. The best HVAC design considers the interrelationship of building systems while addressing energy consumption, indoor air quality, and environmental benefit.

It is well known that the heating and cooling systems have advanced significantly in design and efficiency. For example, today's air conditioners use 30% to 50% less energy to produce the same amount of cooling as air conditioners made in the mid-1970s. Even if your air conditioner is only 10 years old, you may save 20% on your cooling energy costs by replacing it with a newer, more efficient model. A great way to improve the efficiency of heating and cooling systems is to incorporate control strategies that ensure systems are used only when necessary. Common control strategies include programmable thermostats, multiple zones sensors (for example, by dividing your facility up into multiple heating and cooling zones, the HVAC system can deliver more efficient heating and cooling by eliminating inaccuracies from a central sensor point). These strategies can be specified on new heating and cooling systems and retrofitted to older systems as well.

## B. Carry-out RAM & Criticality analysis – Logistic Breakdown (Step 3)

The table (figure 2) below indicates a part of a generic Logistic Breakdown that covers all the HVAC’s equipment. The Logistic Breakdown is done by the ESCO’s RAM engineer during the feasibility phase.

Figure <2: Example detail of the HVAC’s logistic breakdown >

The table (figure 3) below indicates some examples of the EPC’s specifications written by the ESCO’s energy auditor, during the Step 3 of the program concerning the HVAC equipment.

| HVAC’s equipment | Existing Maintenance task | EPC's specification | EPC's energy auditor remarks |
| --- | --- | --- | --- |
| Cooling subsystem |  |  |  |
| 2.1 | Clean the surfaces on the coiling coils, heat exchangers, evaporators and condensing units regularly so that they are clear of obstructions. |  |  |
| 2.2 | Tests and repair leaks in equipment and refrigerant lines |  |  |
| 2.3 |  | Adjust the temperature of the cold air supply air conditioner or heat pump or the cold water supplied by the chiller | A 3°C adjustment can bring a three to five percent energy saving |
| 2.4 |  | Upgrade inefficient chillers |  |

Figure <3: Example detail of the ESCO’s energy auditor specifications >

This table represents a part of the HVAC equipment efficiencies recommen-dations given by [4].

## C. Carry-out RAM & Criticality analysis – Reliability estimation (Step 3)

Figure 4 below shows the pie diagram of one of the 17 most critical centrifugal-pumps for different failure modes. This diagram is based on the ESCO’s audit results.

Figure <4: Failure modes pie of one the most critical centrifugal-pump >

All the failure modes of the 17 most critical centrifugal-pumps are sorted and showed in figure 5 below where Mechanical seal=36%, Overhaul =23.30%, Bearing=11.70% and Maintenance actions=9% of the centrifugal pump failures.

Some Weibull analysis results revisited by the ESCO’s RAM engineer are presented below (figure 6, 7 and 8). The CMMS extract indicate that the seals and bearing (all types) are essentially non repairable items and are currently are replaced after failure. More, after the inefficient maintenance tasks which introduce causes of other new failures, the centrifugal-pumps fail because of the bearings failures.

Figure <5: Failure modes pie diagram of 17 most critical centrifugal-pumps >

The ([9], [10]) documents gives some causes and the preventive actions to be initiated during the EPC’s period in order to eliminate the bearing failures. The same documents specify that there are many reasons that could conduct to the bearing rating life limitation, for example, the heavier loading than has been anticipated, an inadequate or unsuitable lubrication, a careless handling, an ineffective sealing, with resultant insufficient internal bearing clearance. Each one of these factors produces its own particular type of damage and leaves its own special imprint on the bearing. Consequently, by examining a damaged bearing, it is possible, in the majority of cases, to form an opinion on the cause of the damage and to take the requisite action to prevent a recurrence.

The figure 6 shows the linearized Weibull plots for the time between failures of one of the most critical centrifugal-pump.

The Weibull analysis on seals and bearing are performed to find the shape parameters and characteristic life. The shape parameter for seals and bearing is greater than 1 confirming the preventive maintenance actions need (figure 7 and 8). At the same time, the document [11] gives for ball bearing a typical shape parameter β = 1.3 and a characteristic life given is η = 40 000 hours or 55 months; for the seals a typical shape parameter β = 1.4 and a characteristic life η = 25 000 hours or 34 months!

For all aging non reparable items for which the shape parameter is greater than 1; an optimal strategy of replacement could be envisage avoiding the failures and corrective maintenance activities. A condition monitoring and sensors could also be envisaged for seals and bearing after an optimal economic study.

Figure <6: Weibull plot of one of the most critical centrifugal-pump >

| Figure <7: Weibull analysis of seals for all types of the 17 most critical centrifugal-pumps > | Figure <8: Weibull analysis of bearing for all types of the 17 most critical centrifugal-pumps > |
| --- | --- |

## D. Select appropriate maintenance politic and task (Step 4)

The maintenance task description given by the actual CMMS will be analyzed attentively in order to limit the main causes presented in figure 5:“Overhaul” and “Maintenance actions” as 32% of centrifugal-pump failure modes. For the ESCO’s root cause failure analysis the results seems to be solved if: the training is more efficient with an effective use of maintainers (improve job procedure and check), the planning/scheduling means are better avoiding poor performance or a revision of the preventive maintenance frequency is done….

## E. Update the Maintenance Plan (Step 5)

The actual Maintenance Plan analyzed during Step 4 will be reviewed. The results of the Step 3.3 and 3.8 concerning the reliability and lifetime estimation will be included.

## F. Review the EPC’s performances (Step 6)

Proper performance and energy-efficient operation of HVAC systems can only be ensured by taken into account the equipment specifications, maintenance, and cost data, rated condition, age of unit, repair time and materials (T&M) cost data, cost of replacing the unit in emergency situations, efficiency of unit, energy cost for operating the unit.

# Summary & Conclusion

The EPC’s feasibility study for which some results are presented here is not yet finished. The EPC’s RAM engineer works now on the CMMS database and the reliability analysis.  As a simple example, we give here the cooling subsystem that includes today the fans as a critical item. Excessive vibration, noise, reduction of the rotational speed, failure to start of the fan will be unacceptable by the client during the EPC’s duration.  Analyzing in details the root causes, the EPC’s engineer finds that the noise is a result of the bearing failure, and more analyses allows to find that the bearing failure is caused by the loss of lubricant which leads to bearing wear. This is a simple example for which the EPC’s RAM engineer found an answer.

Regrettably, at this stage of the project, a model of aging stress influence is not yet completed elaborate. Today, the risk manager has only some Weibull’s parameters and remaining life MRL estimation of the actual HVAC’s equipment. A stress model adapted to the HVAC equipment and the new energy efficient conditions be developed during the next year based on the “old” HVAC’s failure and maintenance database supplied by the CMMS. In the same time, other reliability databases, for example [5], [6] or [7] will be used or the research’s results that concern the stress influence under the most critical HVAC’s equipment like as: heat-pump and fans (for the air-distribution subsystem), chiller air-cooled rotary (for cooling subsystem), cooler in closed circuit (for the heat rejection subsystem), condensate centrifugal pump (for the cooling pump subsystem), heater exchanger ….

# References

[1] Communication "Energy Efficiency Plan 2011”

[2] Directive 2010/31/EU of the European Parliament

[3] Directive 2002/91/EC of 16/12/2002 on the energy performance of buildings

[4] How to reduce your energy cost: The Vermont Department of Public Service

[5] Eurovent publications

[6] ASHRAE: Service Life and Maintenance Cost Database

[7] FARADIP/ Database

[8] Paul Barringer - Heat Exchanger IRIS Wall Thickness

[9] STEMCO – Bearing failure analysis chart

[10] SKF Bearing failures and causes

[11] Paul Barringer Life Cycle Costs and Weibull